# Shutdown Systems

## Summary

"Shutdown system" is a functional name for the system(s) that bring the reactor to subcritical and keep it there on demand. Architecture and naming differ by reactor type:

- PWR / BWR (LWR): there is normally one Reactor Protection System (RPS) that drives a single set of control rods, plus a diverse means (e.g. ATWS Mitigation System Actuation Circuitry — AMSAC in the US — or boron injection) for the rare scenario where the RPS fails to scram.

- CANDU / PHWR: there are two physically and functionally diverse shutdown systems: SDS1 (mechanical shutoff rods that drop into the calandria) and SDS2 (gadolinium-nitrate poison injection). They are independent in sensors, logic, actuators, power, layout and design teams. CNSC requires both to meet the same safety goal.

- Gas-cooled / SFR / SMR: design-specific; usually still two diverse means.

From an I&C perspective, the relevant function is the trip logic: detect the initiating condition, vote across redundant channels, command the actuators, fail-safe on loss of power, log everything.

## Public sources

| Source | Reference | Repository |
| --- | --- | --- |
| US NRC | 10 CFR 50, Appendix A, GDC 20–25 (protection system design); Reg. Guide 1.118 (periodic testing); BTP 7-19 (D3) | nrc.gov |
| US NRC | NUREG/CR series on RPS reliability and ATWS | NRC NUREG library |
| CNSC (Canada) | REGDOC-2.5.2 — Design of Reactor Facilities; CANDU-specific guidance on SDS1 / SDS2 expectations | nuclearsafety.gc.ca |
| CNSC | Public sections of CANDU 6 / EC6 / ACR licensing files | nuclearsafety.gc.ca |
| AECL / Candu Energy | Public conference papers on SDS1 / SDS2 architecture | OSTI.gov, IAEA INIS |
| IAEA | SSG-39 (I&C design), SSG-30 (safety classification), TECDOC series on RPS | iaea.org |
| Vendor public DCDs | AP1000 DCD Chapter 7, US-EPR FSAR Chapter 7, APR1400 DCD Chapter 7, BWRX-300 / NuScale public docs Chapter 7 | NRC ADAMS |
| Conference papers | NPIC&HMIT, ANS, IAEA technical meetings on RPS modernisation | IEEE Xplore, ANS, IAEA INIS |

## Architectural concepts described in public material

- Redundancy — typically four independent channels in LWR RPS, two diverse systems in CANDU.

- Voting — 2-of-4 coincidence is the LWR norm; 2-of-3 per system in CANDU SDS1 / SDS2.

- Fail-safe / energise-to-trip vs de-energise-to-trip — most reactor-scram designs are de-energise-to-trip (rods fall under gravity / spring force on loss of power to the holding magnets).

- Manual scram — hardwired path that bypasses the digital logic.

- Bypasses — per-channel bypass with continuous indication and time limits.

- On-line testing — each channel testable while the others maintain the trip function (single-failure-tolerant during test).

- Diversity (D3) — the digital RPS is paired with a diverse means using different technology, different signals, or different vendor, to defeat common-cause software failure.

- Independence — physical separation, electrical isolation, separate Class 1E power divisions.

- Determinism — every trip path has a bounded, demonstrated worst-case response time.

## Information not publicly available

- Vendor application logic that implements the trip equations on any given plant.

- Setpoint analyses, channel-uncertainty calculations, and their inputs.

- Common-cause-failure (CCF) coping analyses below the architecture level.