# Eagle-21

## Summary

Eagle-21 is a Westinghouse digital protection / process-protection platform, introduced in the late 1980s and 1990s as a replacement for the original analog 7300 process-protection racks in Westinghouse PWRs. It implements the standard four-channel reactor protection logic (overtemperature ΔT, overpower ΔT, low pressuriser pressure, etc.) in microprocessor-based modules and was the first NRC-approved digital protection upgrade for the US PWR fleet. Functionally: redundant channels, two-out-of-four coincidence, manual bypass with annunciation, deterministic scan time, EMI- and seismic-qualified.

## Public sources

| Source | Reference | Repository |
| --- | --- | --- |
| US NRC | Westinghouse WCAP topical reports on Eagle-21; non-proprietary "(NP)" variants are public | NRC ADAMS, full-text search "Eagle-21 WCAP" |
| US NRC | Plant-specific Safety Evaluation Reports approving Eagle-21 installation or extended power uprate (e.g. records for Sequoyah, Watts Bar, Diablo Canyon, Comanche Peak) | NRC ADAMS |
| US NRC | Generic Letter 95-02 era discussion of microprocessor protection upgrades | NRC ADAMS |
| Westinghouse | Public product overview pages | westinghousenuclear.com |
| Conference papers | NPIC&HMIT and ANS Annual proceedings on PWR RPS upgrades | OSTI.gov, ANS publications |
| EPRI | Reports on digital RPS lessons learned | epri.com |

## Architectural concepts described in public material

- Four protection channels (sets/trains) with electrical and physical separation.

- 2-of-4 coincidence trip logic for primary protection functions.

- Process Protection Cabinets containing dedicated digital modules per function.

- Self-diagnostics — continuous on-line testing, channel-by-channel bypass without losing the trip function.

- Defence-in-depth — Eagle-21 covers the protection function; reactor control is on a separate (often analog or different-vendor) system.

- Setpoint methodology per the ISA RP67.04 / ISA-S67.04 family, integrated into Eagle-21 channel-uncertainty calculations.

## Information not publicly available

- Proprietary versions of the WCAP reports (the non-(NP) variants).

- Application setpoints, channel-statistical-allowance calculations, and qualification test data.

- Current source code and firmware.