# N4 Control System

## Summary

"N4" refers to the fourth generation of French 1450 MWe PWRs (Chooz B-1/B-2 and Civaux 1/2, commissioned 1996–2002). It was the first French fleet generation built around a fully computerised control room and a digital control system supplied by what was then Framatome and Schneider, with operator interaction through a CRT-based control workstation called KIC / SCIP rather than analog hard panels. The protection (Class 1E) and control (non-1E) systems are architecturally distinct: protection is implemented on the SPIN family digital protection system (Système de Protection Intégré Numérique); control is implemented on the N4 process control system. Lessons from N4 fed directly into the EPR control-room design.

## Public sources

| Source | Reference | Repository |
| --- | --- | --- |
| EDF | Public technical communications on the N4 fleet | edf.fr |
| Framatome | Heritage product pages on SPIN and N4 | framatome.com |
| ASNR (formerly ASN, France) | Public regulator opinions on N4 plants | asnr.fr |
| IRSN | Technical notes on French fleet I&C | irsn.fr |
| OECD/NEA | Reports on advanced control rooms (N4 is a recurring case study) | oecd-nea.org |
| Conference papers | NPIC&HMIT (proceedings 1996–2003), ENC, IAEA technical meetings on advanced control rooms | IEEE Xplore, IAEA INIS, OSTI.gov |
| IAEA TECDOCs | "Modern instrumentation and control for nuclear power plants" series | IAEA publications |

## Architectural concepts described in public material

- Fully digital, highly automated control room — two operator workstations and a Safety Panel; no traditional wall of analog meters.

- SPIN protection system — separate from the control system, four independent protection trains, 2-of-4 voting, qualified to French RCC-E rules.

- Hierarchical control system — sensor / process I/O level → unit / loop control level → unit-wide supervisory level → operator workstations.

- Strong separation between safety and non-safety, with hardware-enforced one-way data paths from safety to non-safety.

- Operator HMI based on the "soft control" concept with hierarchical mimic displays, alarm reduction and computerised procedures — many publicly published HFE lessons learned in EPR / EPR2 trace back to N4 operating experience.

## Information not publicly available

- Detailed application code for N4 process control or SPIN protection.

- Vendor qualification dossiers.

- Plant-specific configuration and setpoint information.