# Siemens-Related Platforms in Nuclear I&C

"Siemens PLC" in a nuclear I&C context can refer to three distinct platform families with very different qualification status and tool chains.

## 1. TELEPERM XS (TXS)

- Heritage Siemens KWU; owned by Framatome since the Areva NP transition.

- Nuclear-qualified Class 1E / Category A platform, qualified to IEC 61513 / IEC 60880.

- Engineered with the dedicated Function Diagram / SPACE tool; validated with SIVAT.

- Not TIA Portal. Not Step 7. Not the STL/SCL/LAD as written for industrial PLCs.

- Acquisition path: Framatome under licence.

- See ../02_systems/teleperm-xs/ for fuller treatment.

## 2. SPPA-T2000 / SPPA-T3000

- Siemens Energy distributed control system for power-plant operational control (turbine, balance of plant, non-safety reactor-side functions).

- Not Class 1E. Used widely for non-safety plant control in nuclear plants.

- Engineering performed in the SPPA-T3000 application server / workbench — not TIA Portal.

- Public manuals available on Siemens Industry Online Support after registering a SiePortal account.

## 3. SIMATIC S7-1500F (and the older S7-400F) with TIA Portal Safety Advanced

- General-purpose functional-safety PLC, certified to IEC 61508 SIL 3 by TÜV.

- Not by itself qualified to IEC 60880 / IEC 61513 Category A. It can be used for selected non-safety or lower-category functions on a nuclear plant; for Class 1E protection it would require a project-specific qualification campaign that is rarely undertaken.

- This is the only one of the three for which public manuals, sample projects, and source code are downloadable freely (with a registered Siemens account).

## Public Siemens documentation

The following are downloadable from Siemens Industry Online Support (support.industry.siemens.com) with a free SiePortal account:

- SIMATIC S7-1500 / ET 200MP system manual

- SIMATIC Safety — Configuring and Programming (programming manual for F-CPUs)

- STEP 7 Safety Advanced V18 / V19 manual

- Programming Guideline for S7-1200 / 1500

- SCL / LAD / FBD reference manuals

- Safety-related TÜV certificates for the F-CPUs

- Application examples ("Application IDs"): worked examples for safety patterns (E-stop, two-hand control, muting, etc.)

Public Siemens code samples are published at github.com/siemens (Industrial Edge, OpenPLC adapters, library samples), generally under permissive licences.

## Qualification status comparison

| Platform | Owner today | Nuclear Class 1E / IEC 60880 Cat. A | IEC 61508 SIL 3 (industrial) | Engineering tool |
| --- | --- | --- | --- | --- |
| TELEPERM XS | Framatome | Yes | n/a | SPACE / SIVAT (dedicated) |
| SPPA-T2000 / T3000 | Siemens Energy | No | n/a (DCS, not safety PLC) | SPPA-T3000 workbench |
| SIMATIC S7-1500F | Siemens AG | No (project-specific argument required) | Yes (TÜV) | TIA Portal Safety Advanced |